Tender text

FlowBox HKFC20 pump group

WATTS FlowBox HKFC20 6,3 Para SC 15/6

Pump/mixer component group for connecting boilers to mixed heating circuits. Space-saving design, centre distance of 90 mm and pump length of 130 mm. All WATTS pump groups and boiler manifolds are of uniform design. Newly developed 3-way mixing valve (protected design) with very few single parts and sealing surfaces; easily switchable from right to left; actuator can be integrated in various directions. The actuator with temperature control allows the pump mixer component group to be used as a fixed set point controller independent of a boiler control or centralised control.

Very efficient heat insulation, conforming to EnEV (German Energy Saving Ordinance) thanks to patented three-part EPP insulation shell, simple installation. Concealed cable routing behind insulation. All connections G1" male thread, flat sealing. For operation in closed heating networks with non-aggressive media, such as water or water-glycol mixes as per VDI (Association of German Engineers) 2035/ÖNORM (Austrian standard) H 5195. Certified to in-house standard WI10084147N.

Consists of:

- Multi-function isolation valve for supply line with adjustable gravity brake, thermometer (0-120 °C), integrated temperature sensor connector and red handle.

- Multi-function isolation valve for return line with thermometer (0-120 °C), integrated temperature sensor connector and blue handle.

- Wall bracket

- Patented three-part EPP insulation shell

- 3-way mixing valve, protected design

- Actuator with temperature control for fixed set point control

- High-efficiency pump

- Stainless steel pipe

Ball valves: Brass body, spindle and coupling nut.

Mixing valve: Brass body and spindle, EPDM gaskets.

Technical data

Nominal size: DN20

Centre distance: 90 mm

Overall pump length: 130 mm

Height: 293 mm (sealing surface to sealing surface)

Height, including insulation: 310 mm

Width, including insulation: 232 mm

Depth, including insulation: 217 mm

Max. operating pressure: 6 bar
Max. operating temperature: +90° C

Recommended range of application
(at DT=20 K, Dp=100 mbar): max. 48 kW

Kvs value: 6.3

Weight: 4.4 kg

Weight, including packaging: 4.8 kg

Actuator:

3-point signal control

Rotation angle: 90°

Operating time: 135 seconds

Power supply: 230 VAC/50 Hz;

Power consumption: 3,5 VA.

Cable length: 2 m

Pump: Wilo Para SC 15/6

Power supply: 1~230 V +10%/-15%, 50/60 Hz (acc. to IEC 60038)

Protection class: IP X4D

Insulation class: F

Compliant with RoHS

Cable length: 2 m

Type HKFC20 6,3 Para 15/6

Part no.: 10084147

EAN: 4051394142827

Manufacturer: Watts Water Technologies

We reserve the right to make technical changes!

Proof of delivery:

Watts Industries Deutschland GmbH Godramsteiner Hauptstr. 167
76829 Landau
Germany
Phone +49 63 41 96 56-0
Fax +49 63 41 96 56-560 WIDE@wattswater.com

www.wattswater.de