E-ULTRAMIX ELECTRONIC COLLECTIVE THERMOSTATIC MIXING VALVE

e-Ultramix electronic mixing valve

Mechanism controlled by a bimetallic strip and equipped with protective strainers and check valves.

Setting range: 30/70°C

Max. operating pressure: 10 bar

Min. operating pressure: 1 bar

Recommended operating pressure: 2-4 bar

Max. hot water temperature: 85°C

Minimum differential between inlet temperatures: 5°C

ACS approved.

Maintain a constant water temperature in the domestic hot water network.

Bimetallic mechanism with control and remote management.

Equipped with protective strainers and check valves. Remote control and management.

Electronic setting of mixed water temperature.

Setting via central programming unit => safety and temperature maintenance regardless of flow rate and pressure variations.

Automatic thermal disinfection programme to prevent the risk of legionella.

Local or remote retrieval of thermal disinfection data. Export via spreadsheet.

Scald protection in the event of a power cut => programs and users settings are saved regardless of the duration of the power cut.

For installation without loop, specific wiring for activation of drain solenoid valve during disinfection phases.

For installation with loop, external sensor placed on loop circuit, connected to control unit => communication of return water temperature information.