ULTRAMIX FNC with interchangeable cartridge.

Thermostatic mixing valve special security.

The thermostatic mixing valve with the same characteristics than the ULTRAMIX with safety device and allow drawing even in the case of a hot water cut. Special model for the installations with safety showers or emergency eye-washer. Designed to meet all specific water temperature requirements, even at very low sanitary flow rates.

Anti-scalding safety : automatic shut-off in the event of cold water supply failure + authorization to draw cold water (FNC safety function).

Functioning according to a principle of servo-motor.

Water mixing obtained by two independent valves – functioning like two hydraulic relays.

Bimetal control by blue built-in blocking control knob.

Cover in front (gray PVC).

Adjustment range: 10/50°C.

Maximum pressure : 10 bar

Minimum pressure : 1 bar.

Recommended operating pressure : 2-4 bar

Maximum hot water temperature: 85°C.

Minimum temperature variation between inlets : 5°C.

Maximum pressure variation :1,5bar

Approved ACS.

Thermostatic mechanism, integral with the mixing valve cover /pad. No friction from moving metal parts => excellent resistance to scale and remarkable longevity

Check-valves approved NF.

Perfect accessibility, disassembly without tools, easy cleaning without instructions.

Total interchangeability with the current and the old range.